## BOQ
G. BILL OF QUANTITIES
Sl. No. | Description of work | Qty. | Rate | Per. | Amount
1 | Supply, erection, testing & commissioning of floor mounting cubicle type main switch boards comprising as under : (MSB)
Main busbar rating : 500A TPN, copper bus
Incomer :
3-300A Porcelain fuse units to receive ‘TNEB’ incoming supply.
Outgoings :
2-100A Fuse cutouts compartments,
Each equipped with the following :
3-100A Porcelain fuse units
1-125A TPN Fuse switch unit with 63A HRC fuse.
1-(10-60A), KWH meter (3 phase)
4-60A Fuse cutouts compartments,
Each equipped with the following :
3-60A Porcelain fuse units
1-63A TPN Fuse switch unit with 63A HRC fuse.
1-(10-40A), KWH meter (3 phase)
1-floor mounting base frame
1-set of copper earth bus with 2 nos. terminals
1-set of foundation bolts
1-set of lifting hooks
| 1-set of inscription labels |  |  | Set
Note :
a) Refer our G.A. diagram for details
b) Refer our Notes & General technical specifications for construction details.
2 | Supply, erection, testing & commissioning of wall mounting MCB type double door distribution boards for each flats comprising as under : (DBs) (7 compartment model).
Incomers :
1-63A, 4pole, MCB (10 KA)
3-63A, DP, 100mA, ELCBs
Outgoings :
24-6A/16A/20A, SP, MCBs (10 KA)
1-set of common neutral link
1-set of wall mounting frame work
| 1-set of earth bus with two terminals |  |  | Sets
3 | Supply, erection, testing & commissioning of wall mounting MCB type double door distribution boards for flat, comprising as under (CDB-common).
Incomers:
1-63A, 4pole, MCB (10KA)
Outgoings :
18-6A/16A, SP, MCBs (10KA)
1-set of common neutral link
1-set of wall mounting frame work
| 1-set of earth bus with two terminals |  |  | Set
4 | Supply, erection, testing & commissioning of floor mounting type generator switch board comprising with a suitable length of aluminium bus bars and equipped as under: (GSB)
Main bus bar rating :
250A, TPN, Alu. Bus bars
Incomers :
1-250A, 4pole, fuse switch unit
1-set of HRC fuses
Instruments:
1-96 mm sq., flush MISC, ammeter
1-Ammeter selector switch
1-96 mm sq., flush MISC, voltmeter
1-Voltmeter selector switch
1-set of indicating lamps
1-set of potential fuses
1-set of terminal blocks
3 nos. current transformers
Outgoings:
6-125A, auto transfer switch units-ATS
1-set of blank gland plates suitable to receive PVCA cable.
1-set of copper earth bus
| 1-set of floor mounting frame |  |  | Set
5 | Supply, erection, testing & commissioning of on load type, 63A, 4pole, changeover switch and fixed in a suitable wall mounting frame work along with top and bottom adopter boxes, suitable to receive 1-4C x 25 sqmm, PVCA cable. |  |  | Sets
6 | Supply, erection, testing & commissioning of off load type, 16A, 4pole, changeover switch and fixed in a suitable wall mounting frame work along with top and bottom adopter boxes, suitable to receive either cable or copper wires. |  |  | Sets
7 | Supply & laying of the following 1.1KV grade PVC aluminium armoured cable either in ground or wall or as the case may be. The cables while laid on the wall to be concealed by plastering and shall be enclosed by PVC pipes while laid on the ground. Necessary civil work connected with this cable laying are to be considered in the rate and also the relevant clamps and fixing materials are to be considered in the rate. (Exact lengths will be measured at site before starting the work).
| a) 4 core x 25 sqmm PVCA cable. |  |  | M
| b) 31/2 core x 95 sqmm PVCA cable |  |  | M
| c) 3 ½ core x 120 sqmm PVCA cable |  |  | M
| d) 4 core x 16 sqmm PVC copper cable |  |  | M
| e) 4core x 6 sq.mm.PVCA cable. |  |  | M
8 | Supply & providing cable and termination for the above cable with necessary single compression type glands and aluminium sockets and other fixing materials.
| a) 4 core x 25 sqmm PVCA cable. |  |  | Sets
| b) 31/2 core x 95 sqmm PVCA cable |  |  | Sets
| c) 3 ½ core x 120 sqmm PVCA cable |  |  | Set
| d) 4 core x 16 sqmm PVC copper cable |  |  | Set
| e) 4core x 6 sq.mm.PVCA cable. |  |  | Sets
9 | Supply, erection, testing & commissioning DOL ‘type L&T’ make of siemens make starter equipped with 32A TPN fuse switch unit and fixed on a main MS frame to control 3HP or 5HP water pump. |  |  | Sets
10 | Supply & erection of 20A, SP, MCB with 20A, DP, and earth industrial socket (single phase, pin type) and plug on top housed in a suitable MS box for controlling A/C window model units. |  |  | Sets
11 | Supply & fixing of 16A, 3pin combined SP switch and socket mounted, GI in a suitable GI metal box with Neon indicator concealed to wall with hylam perspex sheet cov. |  |  | Sets
12 | Supply & fixing of 6A, 2/3pin combined SP switch and socket mounted in a suitable GI metal box with neon indicator, concealed to wall with hylam/perspex sheet cover. |  |  | Sets
13 | Erection of ceiling fans to 48” sweep complete with suitable length and size of GI down rods (Fans will be supplied by client) ELECTRONIC REGULATORS TO BE SUPPLIED BY CONTRACTOR. |  |  | Sets
14 | Erection of 305mm dia, 100W single phase exhaust fans with wall mounting fixtures and louvers etc., (light duty). |  |  | Sets
15 | Supply & erection of fan hooks clamps with Anchor fastner for suitable sizes for fixing of ceiling fans/chandlier lights. |  |  | Set
16 | Supply & fixing of fan hook box with ‘U’ rod clamps and concealed on the ceiling for fixing of ceiling fans / chandlier lights. |  |  | Sets
17 | Supply & wiring with 3runs of 2.5sqmm PVC multi stranded copper wires for phase neutral and earth and laid in 20mm or 25mm dia, 2mm thick PVC conduit pipes along with necessary bends, junction boxes, clamping arrangements etc., for circuit mains i.e. from respective DBs to various switch boxes. |  |  | M
18 | Supply & wiring with 3runs of 1.5sqmm PVC stranded copper wires for phase, neutral and earth and laid in 20mm dia 2mm thick PVC conduit pipes along with necessary bends, junction boxes, clamping arrangements etc., for the following light, plug, fan points rate is to be inclusive of 6A, SP piono type switches housed in a GI box. (individual controls) All civil works connected with this installation are to be considered in the rate.
| a) Light points |  |  | Pts
| b) Fan points |  |  | Pts
| c) Exhaust fan points |  |  | Pts
| d) Switch box 5A sockets (Board plug) |  |  | Pts
| e) Two way control points |  |  | Pts
19 | Supply and fixing of skirt level 6A, single phase socket points. |  |  | Pts
20 | Supply & wiring with 2runs of 4sqmm PVC stranded copper wire and 1run of 2.5sqmm PVC copper stranded wires for phase, neutral and earth laid in 25m dia, 2mm thick PVC conduit pipes along with necessary bends, junction boxes, clamping arrangements etc., for connecting all 16A and 20A single phase power sockets from the respective DBs. |  |  | M
21 | Wiring for bell point/buzzer points as described in item 15, with bell switch & buzzer. |  |  | Pts
21 | Supply and Erection of outdoor type light fittings for the total area.
| a) Bulk Head fittings |  |  | Sets
| b) Compound wall light fittings |  |  | Sets
| c) Ceiling mounting light fittings |  |  | Sets
| d) Garden light fittings |  |  | Set
| e) Gate light fittings |  |  | Set
22 | Supply & fixing of wall mounting type distribution point of concealed version and equipped with adequate no of terminals. The terminal block shall mounted on a suitable spacer clamp welded inside the enclosure to have easy access for termination of cables with the following combinations.
| a) Distribution point suitable for 10pair block |  |  | Sets
| b) Do-but 5pair blocks |  |  | Set
| c) Do-but 20pair blocks |  |  | Set
23 | Supply & laying of 20mm dia 2mm thick rigid PVC conduits with all accessories for connecting all telephone outlets concealed to wall / ceiling column etc., |  |  | M
24 | Supply & laying of 2pair telephone cables in the above conduit for connecting all telephone outlets. |  |  | M
25 | Same as above item but 10pair cables |  |  | M
26 | Supply and laying of RG-11, TV cables |  |  | M
27 | Supply & laying of 25mm dia 2mm thick rigid PVC conduits with all accessories for connecting all TV sockets. |  |  | M
28 | Supply & fixing of single pin type TV sockets housed in a suitable metal box concealed to wall. |  |  | Sets
29 | Supply & fixing of 2pin type telephone sockets housed in a suitable metal box concealed to wall.(RJ-11) |  |  | Sets
30 | Earthing system :
a | Providing earthing electrodes with 50mm dia GI pipe, 3000mm long welded to funnel and equipped with reducers, flangers etc., and buried in the ground and filled with salt, charcoal etc., and covered with 500x500x5mm thick chequered plate and generally in conforming to IS:3043 of latest edition. The relevant excavation brick masonry construction of pit etc., are to be included in the rate. |  |  | Sets
b | Providing earthing electrodes with 50mm dia GI pipe, 3000mm long welded to funnel and equipped with 600x600x3.15mm copper plate, etc., and buried in the ground and filled with salt, charcoal etc., and covered with 500x500x5mm thick chequered plate and generally in conforming to IS:3043 of latest edition. The relevant excavation brick masonry construction of pit etc., are to be included in the rate. |  |  | Sets
c | Supply & fixing of 25x3mm copper flats for band earthing. |  |  | M
d | Supply & fixing of No.8SWG copper wire for board earthing. |  |  | M
31 | Supply & fabrication of any MS items along with erection, painting etc., required for this installation. |  |  | M
32 | Excavation of earth upto 1000mm deep in all kinds of soil and back filling with a layer of sand and bricks in all three sides required for the U/G cable, including refilling, ramming, consolidating etc., |  |  | M
33 | Supply & fixing of 3mm thick hylam sheet cover for all provision points. |  |  | M
34 | Supply & laying of the following PVC pipes to lay the under ground cables inside the pipe
| a) 50mm dia size |  |  | M
| b) 100mm dia size |  |  | M
| c) 150mm dia size |  |  | M
35 | Erection only for the following light fittings. (fittings will be supplied as free issue)
| a) 1x40W fluorescent light fittings |  |  | Sets
| b) Chandlier light fittings |  |  | Sets
| c) Wall bracket ‘GLS’ light fittings |  |  | Sets
| d) Ceiling mounting ‘GLS’ light fitting |  |  | Sets
36 | Erection only of the ‘Geyser’ in the toilet area at individual flat for the following size.
| a) 1000W rating |  |  | Set
| b) 1500W rating |  |  | Sets
| c) 2000W rating |  |  | Set
| d) 2500W rating |  |  | Set
| e) 5000W rating (instant type) |  |  | Set
37 | Supply & fixing of 1x40W fluorescent light fittings along with lamp, starter and choke to philips cat ref:TMC21/236 |  |  | Set
38 | Supply & fixing of 2x40W fluorescent light fittings along with lamp, starter, and choke to Philips cat ref:TMC21/236 |  |  | Set
39 | Supply & fixing of 60W ‘GLS’ bulk head fitting to Philips cat ref:NXC-11/60W |  |  | Set
40 | Supply & fixing of gate light fittings to Philips cat ref:HPC11/80 with 80W mercury vapour lamp and all other accessories including wiring to light fittings with 3runs of 14/0.3mm PVC copper wires, drawn inside suitable size MS conduit, from the pillar bottom including provision of control switch and fuse cutouts recessed in weather proof metal box. |  |  | Sets
41 | Supply & fixing of outdoor light fittings (Floor light model) to Philip cat ref:NVC53 with 500W halogen lamp, other control gear etc., and fixed on the suitable MS brackets |  |  | Sets
42 | Supply & laying of 1-3.5C x 95 Sqmm, PVCA cable along with necessary fixing brackets for connecting 62.50KVA, DG Set and control panel. |  |  | M
43 | Providing necessary cable end terminations along with necessary glands and sockets. |  |  | Sets
44 | Erection of 62.50 KVA, DG Set control panel. |  |  | Set
45 | Supply and fixing of 19mm dia., copper pipe with 1500mm long and fixed on the top of building. (lightning spikes) |  |  | Sets
46 | Supply and fixing of 25 x 3mm copper flat for down conductors along with necessary fixing brackets. |  |  | M
47 | Supply and fixing of 25 x 3mm copper flate for horizontal conductors along with necessary fixing brackets. |  |  | M
48 | Supply and fixing of necessary test terminal blocks. |  |  | Set
49 | Supply and providing necessary 50mm dia., GI pipe earth electrode, 3000mm long, along with necessary funnels, nipples, side brackets, etc., for the above lightning spikes along with necessary civil works including digging, sand filling and salt / coke etc. and covered with either 5mm thick chequered plates of 500 x 500mm size or equivalent size of RCC slabs. |  |  | Set
50 | Co-ordinaiton & liasioning with CEIG authorities for obtaining drawing approval & safety certificate for 62.50KVA, DG Set and organising site inspection by the authorities. All the incidental expenses are to be included in the item. |  |  | L.S.
51 | Co-ordinaiton & liasioning with CEIG authorities for obtaining drawing approval & safety certificate for 1 Set of 3.75KW, Lifts and organising site inspection by the authorities. All the incidental expenses are to be included in the item. |  |  | L.S.
52 | Co-ordinaiton & liasioning with TNEB authorities for obtaining LT load sanction & avail LT supply at premises for various flat owners. All the incidental expenses are to be included in the item. |  |  | L.S.
Note :
1 | Prices should include-All duties, taxes, freight, works contract tax if applicable etc.,
2 | KWH meters in main panel will be supplied by TNEB ‘MRT’ division.
3 | All necessary minor civil works connected with this electrical contracting work such as chipping, chasing, etc., should also be included in the above prices.
TOTAL

## Abstract
PRICE SUMMARY
G. BILL OF QUANTITIES
Sl. No. | DESCRIPTION | AMOUNT IN RS.
1 | ELECTRICAL INSTALLATION WORK COMPRISING L.T. POWER, LIGHTING DISTRIBUTION SYSTEM, POWER CABLINGS, TELEPHONE CONDUITS, LIGHTNING PROTECTION SYSTEM, LIGHT FITTINGS, POWER SOCKETS, LIGHTING SOCKETS, EARTHING SYSTEM, ETC.
TOTAL